## Worksheet 1
Component | Damage mechanisms | References | Hazard | Exposure | Vulnerability | Scale of analysis
[6 empty] | Spatial | Temporal
Lines and cables | Damage to buried ends of overhead lines, sweeping away of underground cables | Holmes (2012), Nicolas et al. (2019), FEMA (2022) | Flow velocity, duration of inundation, debris/sediments amount | Number and length of lines and cables | Installation depth, carrying capacity | Micro | Short-term
Towers and poles | Foundation structural damage, subversion, displacement | Powerlink Queensland (2011), Booth et al. (2017), Karagiannis et al. (2017), Feeney et al. (2022) | Flow velocity, duration of inundation, debris/sediments amount | Number and height of towers and poles | Installation depth, carrying capacity | Micro | Short-term
Substations and cabins | Cabin and control house water intrusion, switchyard washing away, communication failure, de-energization, fire, and explosion | Abi-Samra and Malcolm (2011), Powerlink Queensland (2011), Holmes (2012), Ward (2013), Boggess et al. (2014), Karagiannis et al. (2017) | Inundation depth, debris/sediments amount | Number and area of substations and cabins | Electrical equipment height, flood protection system, pumping equipment installation, air vents height, voltage level | Micro | Short-term
Power plants | Backup generators damage, destruction of cooling towers, facilities water intrusion, foundation structural damage | Srinivasan and Gopi Rethinaraj (2013), McCall et al. (2016), New York Power Authority et al. (2017), Nicolas et al. (2019) | Inundation depth, flow velocity, duration of inundation, debris/sediments amount | Number and area of power plants | Electrical equipment height, flood protection system, nominal capacity | Micro | Short-term